# ORDINANCE NO. 2077

AN ORDINANCE ESTABLISHING A PROGRAM OF BACKFLOW PREVENTION WITH CONTAINMENT AND PROVIDING FOR THE ADMINISTRATION AND ENFORCEMENT OF THE PROGRAM AND PROVIDING PENALTIES FOR NONCOMPLIANCE AND PROVIDING FOR THE ESTABLISHMENT OF FEES BY COUNCIL RESOLUTION.

WHEREAS, Iowa Administrative Code/Public Health Department 641-25.5(135) requires cities with populations of 15,000 or greater to enact a backflow prevention program with containment; and

WHEREAS, the City of Fort Dodge wishes to protect the quality and safety of the public water supply.

NOW, THEREFORE, BE IT ORDAINED BY THE CITY COUNCIL OF THE CITY OF FORT DODGE, IOWA:

Preamble.  Iowa Administrative Code/Public Health Department 641-25.5(135) requires the city to enact a backflow prevention program with containment.

Purpose.  The purpose of this chapter is to provide administration and enforcement procedures, to provide for evaluation of existing and new water services, to provide for the installation and regular maintenance of required protective devices, and to provide for penalties for violation of the requirements.

Cross connection control-containment.

(a)   Definitions.  For the purpose of this section, the following definitions supersede definitions given elsewhere in this article or in the plumbing code and shall apply only to this section:

Administrative authority  means the city water department and building official.

Approved backflow prevention assembly for containment.  Approved backflow prevention assembly for containment means a backflow prevention assembly which is approved by the University of Southern California-Foundation for Cross Connection Control and Hydraulic Research.  The approval listing shall include the limitations of use based on the degree of hazard.  The backflow prevention assembly shall also be listed by the International Association of Plumbing and Mechanical Officials (IAPMO) or by the American Society of Sanitary Engineering (ASSE) as having met the requirements of one of the standards listed below.

Standard			Product Covered

______________________________________________________

ANSI/ASSE* 1013-1999		Reduced Pressure Principle									Backflow Preventers

ANSI/ASSE* 1015-1999		Double Check Backflow										Prevention Assembly

ANSI/ASSE* 1047-1999		Reduced Pressure Detector								Backflow Preventer

ANSI/ASSE* 1048-1999		Double Check Detector									Assembly Backflow Preventer

ANSI/AWWA ( C510-97		Double Check Valve Backflow									Prevention Assembly

ANSI/AWWA ( C511-97		Reduced-Pressure Principle								Backflow Prevention Assembly

( American National Standards Institute, 1819 L Street NW, Washington, DC 20036

( American  Society of Sanitary Engineering, 28901 Clemens Road, Ste 100, Westlake, OH    44145

(  American Water Works Association, 6666 West Quincy Avenue, Denver, CO  80235

Approved backflow prevention assembly for containment in a fire protection system  means a backflow prevention assembly to be used in a fire protection system which meets the requirements of Factory Mutual Research Corporation (FM) and Underwriters' Laboratories, Inc. (UL), and the requirements of the city fire code and building code, in addition to the requirements of subsection (g)(1). Devices sized smaller than 2 1/2 inches, which have not been listed by Underwriters' Laboratories, Inc. (UL) and tested by Factory Mutual Research Corporation (FM), may be allowed if they meet the requirements of the city fire code and building code.

Auxiliary water supply  means any water supply on or available to the premises other than the water purveyor's approved public water supply, such as but not limited to a private well, pond, or river.

Containment  means a method of backflow prevention which requires the installation of a backflow prevention assembly at the water service entrance.

Cross connection  means any actual or potential connection or arrangement, physical or otherwise, between a potable water supply system and any plumbing fixture or tank, receptacle, equipment, or device, through which it may be possible for non-potable, used, unclean, polluted, and contaminated water or other substance to enter into any part of such potable water system under any condition.

Customer  means the owner, operator, or occupant of a building or property which has a water service from a public water system, or the owner or operator of a private water system which has a water service from a public water system.

Degree of hazard  means the rating of a cross connection or water service which indicates if it has the potential to cause contamination or pollution.

Double check valve backflow prevention assembly  means a backflow prevention device consisting of two independently acting internally loaded check valves, four properly located test cocks, and two isolation valves.

High hazard cross connection  means a cross connection which may cause an impairment of the quality of the potable water by creating an actual hazard to the public health, through poisoning or through the spread of disease by sewage, industrial fluids, or waste.

Isolation  means a method of backflow prevention in which a backflow prevention assembly is located at the cross connection rather than at the water service entrance.

Low hazard cross connection  means a cross connection which may cause an impairment of the quality of potable water to a degree which does not create a hazard to the public health, but which does adversely and unreasonably affect the aesthetic qualities of such potable waters for domestic use.

Reduced pressure principle backflow prevention assembly  means a backflow prevention device consisting of two independently acting internally loaded check valves, a different pressure relief valve, four properly located test cocks, and two isolation valves.

Registered backflow prevention assembly technician  means a person who is registered by the state to test or repair backflow prevention assemblies and report on the condition of those assemblies.

Thermal expansion  means volumetric increase of water due to heating resulting in increased pressure in a closed system.

Water service,  depending on the context, means the physical connection between a public water system and a customer's building, property, or private water system, or the act of providing potable water to a customer.

Water department  means the city water department.

(b)   Administrative authority.

(1)   Water department or the building official shall have the right to enter, with the consent of the customer or upon the basis of a suitable warrant issued by a court of appropriate jurisdiction, any property to inspect for possible cross connections.

(2)   Water department shall maintain records of cross connection hazard surveys and the installation, testing, and repair of all backflow prevention assemblies installed for containment purposes.

(c)   New water services.  New water services shall comply with the following:

(1)   Plans shall be submitted to water department for review on all new water services in order to determine the degree of hazard.

(2)   The water department shall, in consultation with the building official, determine the type of backflow prevention assembly required for containment based on the degree of hazard.

(3)   The building official shall inspect the installation of the required backflow prevention assembly for containment before the initiation of water service.

(d)   Existing water services.  Existing water services shall comply with the following:

(1)   Upgrades or reconstruction of existing water services shall be treated as new water services for the purpose of this section.

(2)   The water department in consultation with the Plumbing Inspector shall, on the basis of information received from customers or gathered through on-premises investigations or surveys, determine the type of backflow prevention assembly required for containment based on the degree of hazard.

(3)   Within the timeframe specified in writing by the water department, the customer shall install a backflow prevention assembly for containment required by the water department.

(4)   For existing water services, the water department may inspect the premises to determine the degree of hazard. When high hazard cross connections are found, water department shall, at it sole discretion:

a.   Develop a schedule of compliance which the customer shall follow; or

b.   Terminate the water service until a backflow prevention assembly for containment required by the water department has been installed.

(5)   Failure of the water department to notify a customer that the customer is believed to have a high hazard cross connection and that the customer shall install backflow prevention assemblies for containment in no way relieves a customer of the responsibility to comply with all requirements of this section.

(e)   Customer.  Responsibilities of the customer shall be as follows:

(1)   The customer shall be responsible for ensuring that no cross connections exist without approved backflow protection within his or her premises starting at the point of service from the public potable water system.

(2)   The customer shall, at his or her own expense, cause installation, operation, testing and maintenance of backflow prevention assemblies.

(3)   The customer shall ensure that copies of records of the installation and of all tests and repairs made to the backflow prevention assembly on the approved form within 15 days after testing and/or repairs are completed.

(4)   If a backflow incident occurs, the customer shall immediately notify the water department of the incident and take steps to confine the contamination or pollution.

(f)   Required backflow prevention assemblies for containment for water services.  Backflow prevention assemblies for containment for water services shall be required as follows:

(1)   An air-gap or an approved reduced pressure principle backflow prevention assembly is required for water services having one or more cross connections which the administrative authority has classified as high hazard.

(2)   An approved double check valve assembly is required for water services having no high hazard cross connections but having one or more cross connections which the water department has classified as low hazard.

(g)   Required backflow prevention assemblies for containment for fire protection systems.  Backflow prevention assemblies for containment for fire protection systems shall be required as follows:

(1)   A reduced pressure principle backflow prevention assembly shall be installed on all new and existing fire protection systems which the water department determines to have any of the following:

a.   Direct connections from public water mains with an auxiliary water supply on or available to the premises for pumper connection.

b.   Interconnections with auxiliary supplies such as reservoirs, rivers, ponds, wells, mills, or other industrial water systems.

c.   Use of antifreezes or other additives in the fire protection system.

d.   Combined industrial and fire protection systems supplied from the public water mains only, with or without gravity storage or pump suction tanks.

e.   Any other facility, connection, or condition which may cause contamination.

(2)   A double check valve assembly will be required for all other fire protection systems. The double check valve assembly shall be required on all new systems at the time of installation and on existing systems at the time that they are upgraded.

(3)   Submittal of proposed backflow prevention devices to the water department does not relieve the designer or the sprinkler contractor of the responsibility of submitting plans, including backflow prevention devices to the fire marshal for approval.

(h)   Backflow prevention assembly technicians.  A backflow prevention assembly technician registered by the state and City shall include his or her registration number on all correspondence and forms required by or associated with this section.

(i)   Registered backflow prevention assembly technician noncompliance.  Noncompliance with any of the following by a registered technician shall be grounds for reporting such individual to the state department of public health:

(1)   Improper testing or repair of backflow prevention assemblies.

(2)   Improper reporting of the results of testing or of repairs made to backflow prevention assemblies.

(3)   Failure to meet registration requirements.

(4)   Related unethical practices.

(j)   Installation of backflow prevention assemblies.  Backflow prevention assemblies shall be installed in compliance with the following:

(1)   The required backflow prevention assemblies for containment shall be installed in horizontal plumbing immediately following the meter or as close to that location as deemed practical by the water department. In any case, it shall be located upstream from any branch piping. Installation at this point does not eliminate the responsibility of the customer to protect the water supply system from contamination or pollution between the backflow prevention assembly and the water main.

(2)   Reduced pressure principle backflow prevention assemblies shall be installed so as to be protected from flooding.

(3)   Reduced pressure principle backflow prevention assemblies shall not be installed in underground vaults or pits.

(4)   All backflow prevention assemblies shall be protected from freezing. Those devices used for seasonal water services may be removed in lieu of being protected from freezing; however, the devices must be reinstalled and tested by a registered backflow prevention technician prior to service being reactivated.

(5)   If hot water is used within the water system, thermal expansion shall be provided for when installing a backflow prevention assembly for containment.

(6)   Provisions shall be made to convey the discharge of water from reduced pressure principle backflow prevention assemblies to a suitable drain.

(7)   No backflow prevention assemblies shall be installed in a place where it would create a safety hazard, such as but not limited to over an electrical panel or above ceiling level.

(8)   If interruption of water service during testing and repair of backflow prevention assemblies for containment is unacceptable, another backflow prevention assembly, sized to handle the temporary water flow need during the time of test or repair, should be installed in parallel piping.

(9)   All backflow prevention assemblies shall be installed so that they are accessible for testing as stated in the City Plumbing Code.

(10)   All shutoff valves shall conform with the current edition of the Manual of Cross-Connection Control (University of Southern California) requirements for either ball or resilient seat gate valves at the time of installation. Ball valves shall be used on assemblies installed in piping two inches and smaller and resilient seat gate valves on assemblies installed in piping larger than two inches.

(11)   Location and protection of the containment assembly shall be approved by the water department prior to installation.

(k)   Testing of backflow prevention assemblies.  Backflow prevention assemblies shall be tested as follows:

(1)   Testing of backflow prevention assemblies shall be performed by a registered backflow prevention assembly technician. The costs of tests required in the subsections (k)(2) through (5) of this section shall be borne by the customer.

(2)   Backflow prevention assemblies shall be tested upon installation and tested and inspected at least annually.

(3)   Backflow prevention assemblies which are in place, but have been out of operation for more than three months, shall be tested before being put back into operation. Backflow prevention assemblies used in seasonal applications shall be tested before being put into operation each season.

(4)   Any backflow prevention assembly which fails a periodic test shall be repaired or replaced. When water service has been terminated for noncompliance, the backflow prevention assembly shall be repaired or replaced prior to the resumption of water service. A registered backflow prevention assembly technician shall retest Backflow prevention assemblies immediately after repair or replacement.

(5)   The water department or the building official may require backflow prevention assemblies to be tested at any time in addition to the annual testing requirement.

(6)   The registered backflow prevention assembly technician shall report the successful test of a backflow prevention assembly to the customer and to the water department on the form provided by the water department within 15 days of the test.

(7)   The water department or the building official may require, at the owner's expense, additional tests of individual backflow prevention assemblies as it shall deem necessary to verify test procedures and results.

(l)   Repair of backflow prevention assemblies.  Backflow prevention assemblies shall be repaired in accordance with the following:

(1)   All repairs to backflow prevention assemblies shall be performed by registered backflow prevention assembly technicians.

(2)   The registered backflow prevention assembly technician shall not change the design, material, or operational characteristics of a backflow prevention assembly during repair or maintenance, and shall use only original manufacturer replacement parts.

(3)   The registered backflow prevention assembly technician shall report the repair of a backflow prevention assembly to the customer and to the water department on the form provided by the water department within 15 days of the repair. The report shall include the list of materials or replacement parts used.

(4)   Any time fire services are discontinued for a period of time longer than necessary to test the device, the tester is required to notify the fire chief's office that the fire services are shut off for repair.

(m)   Customer noncompliance.  The water service may be discontinued in the case of noncompliance with this section. Noncompliance includes but is not limited to the following:

(1)   Refusal to allow the water department and/or the plumbing inspection division personnel access to the property to inspect for cross connections.

(2)   Removal of a backflow prevention assembly which has been required by the water department.

(3)   Bypassing of a backflow prevention assembly which has been required by the water department.

(4)   Providing inadequate backflow prevention when cross connections exist.

(5)   Failure to install a backflow prevention assembly which has been required by the water department.

(6)   Failure to test and/or properly repair a backflow prevention assembly as required by the water department.

(7)   Failure to comply with the requirements of this section.

(n)   Replacements.  Replace listed RPZ with stainless steel dual check with an atmospheric opening complying with the City of Fort Dodge plumbing code.

Registration of backflow prevention assembly technician.  Prior to performing testing or repair of any backflow prevention device which receives its water supply from the City of Fort Dodge public water system, a technician shall first register with the City Clerk and shall provide proof of current registration under Iowa Administrative Code 641-26.

Board of Appeals.  Any person aggrieved by a decision of the water department/building official pursuant to this ordinance may appeal to the Board of Appeals pursuant to and in the manner provided for in Chapter 14.56 of the Fort Dodge Municipal Code.

Fees.  The fees for activities and services performed by City of Fort Dodge in carrying out its responsibilities under this ordinance shall be set by the City Council by resolution.

Violation-Penalty.  Anyone violating any of the provisions of this ordinance shall upon conviction, be subject to the penalties in accordance with Section 1.20.020 of the Fort Dodge Municipal Code.

Repealer.  All ordinances and parts of ordinances in conflict with this ordinance are hereby repealed.

Effective Date.  This Ordinance shall be in full force and effect following its passage and publication as provided by law.

Severability Clause.  If any section, provision or part of this Ordinance shall be adjudged invalid or unconstitutional, such adjudication shall not affect the validity of the Ordinance as a whole or any section, provision, or part thereof not adjudged invalid or unconstitutional.

The above Ordinance passed and adopted by the City Council of the City of Fort Dodge, Iowa this 11th day of June, 2007.

CITY OF FORT DODGE

BY:

Terry J. Lutz, Mayor

ATTEST

_________________________

Penny Clayton, City Clerk

Published in the Messenger the _____ day of _______________________, 2007.